## raw_ops_events_v3_clean
event_id | day_key | event_type | event_group_id | event_title_short | date_start | time_start_local | date_end | time_end_local | duration_hours | duration_class | location_text | extent_class | affected_regions_count | affected_municipalities_n | event_summary_short | raw_description_150_200w | sector_primary | sector_secondary | hazard_family | hazard_subtype | source_url_primary | source_url_secondary_list | source_code | source_name_primary | source_name_page_ref | source_document_type | source_type | source_reliability_rank | sc_env_0to3 | sc_E_0to3 | sc_D_0to3 | sc_T_0to3 | sc_severity_0to5 | sc_extent_0to5 | sc_duration_0to5 | sc_cascade_0to5 | sc_confidence_0to5 | sc_notes
e_ops_2024_0409_001 | 2024_04_09 | E_OPS |  | ČHE Avče unit trip generator breaker fuse | 2024-04-09 | 08:06 | 2024-04-09 | 09:59 | 01:53 | 1–6h | ČHE Avče | local | 1 |  | Pumped-storage unit trip | Pumped-storage unit trip. Event recorded as 'ČHE Avče unit trip generator breaker fuse'. Location: ČHE Avče. Coded as TECH / EQUIPMENT_FAILURE. | E |  | TECH | EQUIPMENT_FAILURE |  |  | ELES_2024_W15 | ELES weekly report W15 | events | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 2 | 1 | 5
e_ops_2024_0409_002 | 2024_04_09 | E_OPS |  | HE Doblar 2 unit 1 trip governor fault | 2024-04-09 | 17:01 | 2024-04-09 | 17:47 | 00:46 | <1h | HE Doblar 2 | local | 1 |  | Hydro unit trip | Hydro unit trip. Event recorded as 'HE Doblar 2 unit 1 trip governor fault'. Location: HE Doblar 2. Coded as TECH / TURBINE_GOVERNOR_FAULT. | E |  | TECH | TURBINE_GOVERNOR_FAULT |  |  | ELES_2024_W15 | ELES weekly report W15 | events | pdf | official_report | A | 0 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 5
e_ops_2024_0410_001 | 2024_04_10 | E_OPS |  | STATCOM voltage support activation | 2024-04-10 | 12:00 | 2024-04-10 | 12:45 | 00:45 | <1h | Transmission voltage control asset | regional | 1 |  | Reactive power stabilization event | STATCOM device was activated to provide reactive power support and voltage stabilization following temporary oscillatory behaviour in the transmission grid. The intervention indicates localized voltage stress but prevented further instability. | E |  | TECH | VOLTAGE_CONTROL_EVENT |  |  | ELES_2024_04 | ELES monthly operational report (April 2024) | p.II | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 4 | Operational mitigation
e_ops_2024_0412_001 | 2024_04_12 | E_OPS | CL_2024_0412_MARIBOR | TR T411 400/110 kV Maribor trip differential protection | 2024-04-12 | 02:40 | 2024-04-19 | 11:47 | 177:07 | >3d | RTP Maribor | regional | 1 |  | Long-duration backbone transformer outage | 400/110 kV transformer T411 in RTP Maribor tripped due to differential protection activation. The transformer remained unavailable for more than seven days. Although no cascading blackout occurred, the prolonged unavailability reduced redundancy at the 400/110 kV interface and required operational reconfiguration of power flows. | E |  | TECH | PROTECTION_TRIP |  |  | ELES_2024_04 | ELES monthly operational report (April 2024) | p.II | pdf | official_report | A | 0 | 3 | 0 | 0 | 4 | 2 | 5 | 2 | 5 | Long HV outage
e_ops_2024_0415_001 | 2024_04_15 | E_OPS |  | HE Mariborski otok unsuccessful start | 2024-04-15 | 00:00 | 2024-04-29 | 00:00 | 336:00 | >3d | HE Boštanj | regional | 1 |  | Extended hydro unit outage | Hydro power plant Boštanj experienced extended unavailability due to internal technical malfunction. Although the event did not trigger grid instability, it reduced domestic hydro generation availability during mid-April and required balancing adjustments within the system. | E |  | TECH | GENERATION_TRIP |  |  | ELES_2024_04 | ELES monthly operational report (April 2024) | p.II | pdf | official_report | A | 0 | 2 | 0 | 0 | 3 | 2 | 5 | 1 | 4 | Generation limitation
e_ops_2024_0415_002 | 2024_04_15 | E_OPS | CL_2024_0415_AVCE_GORICA_LIGHTNING | DV 110 kV Avče–Gorica I lightning trip | 2024-04-15 | 16:05 | 2024-04-15 | 16:06 | 00:01 | <1h | Avče–Gorica | local | 1 |  | Lightning corridor trip | Lightning corridor trip. Event recorded as 'DV 110 kV Avče–Gorica I lightning trip'. Location: Avče–Gorica. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W16 | ELES weekly report W16 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5
e_ops_2024_0415_003 | 2024_04_15 | E_OPS | CL_2024_0415_AVCE_GORICA_LIGHTNING | DV 110 kV Avče–Gorica II lightning trip | 2024-04-15 | 16:05 | 2024-04-15 | 16:06 | 00:01 | <1h | Avče–Gorica | local | 1 |  | Lightning corridor trip | Lightning corridor trip. Event recorded as 'DV 110 kV Avče–Gorica II lightning trip'. Location: Avče–Gorica. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W16 | ELES weekly report W16 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5
e_ops_2024_0417_001 | 2024_04_17 | E_OPS | CL_2024_0417_AVCE_GORICA | HE Zlatoličje power limitation intake cleaning | 2024-04-17 | 16:05 | 2024-04-17 | 16:06 | 00:01 | <1h | Avče–Gorica | local | 1 |  | Lightning-induced parallel circuit trip | Simultaneous trip of the 110 kV Avče–Gorica 1 transmission line caused by lightning strike during convective storm conditions. The interruption was extremely short but reflects meteorological forcing affecting transmission infrastructure in western Slovenia. | E |  | ENV | CONV_STORM |  |  | ELES_2024_04 | ELES monthly operational report (April 2024) | p.II | pdf | official_report | A | 2 | 1 | 0 | 0 | 2 | 1 | 1 | 2 | 5 | Parallel corridor
e_ops_2024_0417_002 | 2024_04_17 | E_OPS | CL_2024_0417_AVCE_GORICA | DV 110 kV Avče–Gorica 2 lightning trip | 2024-04-17 | 16:05 | 2024-04-17 | 16:06 | 00:01 | <1h | Avče–Gorica | local | 1 |  | Parallel circuit lightning trip | The second circuit of the Avče–Gorica 110 kV corridor tripped simultaneously due to the same lightning event. The incident represents a corridor-level disturbance affecting parallel infrastructure elements. | E |  | ENV | CONV_STORM |  |  | ELES_2024_04 | ELES monthly operational report (April 2024) | p.II | pdf | official_report | A | 2 | 1 | 0 | 0 | 2 | 1 | 1 | 2 | 5 | Same cluster
e_ops_2024_0424_001 | 2024_04_24 | E_OPS |  | ČHE Avče emergency shutdown turbine pipe damage | 2024-04-24 | 14:04 | 2024-04-24 | 19:24 | 05:20 | 1–6h | ČHE Avče | regional | 1 |  | Emergency shutdown | Emergency shutdown. Event recorded as 'ČHE Avče emergency shutdown turbine pipe damage'. Location: ČHE Avče. Coded as TECH / EQUIPMENT_DAMAGE. | E |  | TECH | EQUIPMENT_DAMAGE |  |  | ELES_2024_W17 | ELES weekly report W17 | events | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 2 | 2 | 5
e_ops_2024_0430_001 | 2024_04_30 | E_OPS |  | ČHE Avče temporary unavailability valve switch fault | 2024-04-30 | 16:00 | 2024-04-30 | 19:00 | 03:00 | 1–6h | ČHE Avče | local | 1 |  | Temporary unavailability | Temporary unavailability. Event recorded as 'ČHE Avče temporary unavailability valve switch fault'. Location: ČHE Avče. Coded as TECH / EQUIPMENT_FAILURE. | E |  | TECH | EQUIPMENT_FAILURE |  |  | ELES_2024_W18 | ELES weekly report W18 | events | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 2 | 1 | 5
e_ops_2024_0430_002 | 2024_04_30 | E_OPS |  | DV 35 kV Divača–Kozina one-sided outage | 2024-04-30 | 20:29 | 2024-04-30 | 20:32 | 00:03 | <1h | RTP Divača | local | 1 |  | 35 kV line outage | 35 kV line outage. Event recorded as 'DV 35 kV Divača–Kozina one-sided outage'. Location: RTP Divača. Coded as UNKNOWN / LINE_OUTAGE. | E |  | UNKNOWN | LINE_OUTAGE |  |  | ELES_2024_W18 | ELES weekly report W18 | events | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 4
e_ops_2024_0505_001 | 2024_05_05 | E_OPS |  | Operational unavailability PB5 TEB | 2024-05-05 | 12:14 | 2024-05-05 | 15:00 | 02:46 | 1–6h | TE Brestanica | local | 1 |  | Thermal unit operational unavailability | PB5 unit at Brestanica Thermal Power Plant became unavailable due to malfunction in the start-up module. The outage lasted nearly three hours and required operational adjustment to maintain balance. Although localized, such events reduce available spinning reserve and increase system sensitivity during peak or stressed periods. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 0 | 4 | Generation-side availability reduction
e_ops_2024_0507_001 | 2024_05_07 | E_OPS |  | Extended unavailability TEŠ Unit 6 | 2024-05-07 | 07:30 | 2024-05-09 | 13:05 | 53:35 | 1–3d | Šoštanj thermal power plant | regional | 1 |  | Generation unit unavailability | Unit 6 at Šoštanj Thermal Power Plant was unavailable for more than two days due to leakage in preheater A7. As a major baseload unit, its prolonged outage required balancing through hydro generation and imports. Long duration and high installed capacity increase systemic relevance, although no cascading instability was reported. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 3 | 2 | 4 | 0 | 4 | Prolonged limitation of major generation unit
e_ops_2024_0509_001 | 2024_05_09 | E_OPS |  | STATCOM outage during large voltage oscillations | 2024-05-09 | 10:04 | 2024-05-09 | 15:01 | 04:57 | 1–6h | Slovenian transmission grid | regional | 1 |  | Voltage instability and reactive support loss | STATCOM unit outage occurred between 10:04 and 15:01 during periods of significant voltage oscillations in the Slovenian transmission grid. The event was documented in the ELES monthly operational report. The outage temporarily reduced voltage stabilization capability in the affected transmission area. Grid operators maintained system stability through operational control measures. No end-user power outages were reported during the event. | E |  | TECH | EQUIPMENT_FAILURE |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 2 | 2 | 0 | 4 | Official ELES operational event; regional voltage-control device outage; no documented public service interruption or cross-sector effect.
e_ops_2024_0509_002 | 2024_05_09 | E_OPS |  | HE Dravograd unit 3 trip excitation fault | 2024-05-09 | 10:13 | 2024-05-09 | 12:25 | 02:12 | 1–6h | HE Dravograd hydropower plant | local | 1 |  | Generation unit outage at hydropower plant | A generation unit (unit 3, approximately 9.6 MW capacity) at the Dravograd hydropower plant experienced an outage due to a fault in the excitation system. The outage lasted from 10:13 to 12:25 and was documented in the ELES monthly operational report. The incident temporarily reduced generation output but did not cause broader grid instability. | E |  | TECH | GENERATION_TRIP |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 2 | 0 | 4 | Official ELES report; single generation unit trip at HE Dravograd; local generation loss; short duration; no documented cascade.
e_ops_2024_0511_001 | 2024_05_11 | E_OPS |  | 110 kV line outage Trbovlje–Beričevo I | 2024-05-11 | 00:58 | 2024-05-11 | 08:07 | 07:09 | 6–24h | RTP Trbovlje transmission node | regional | 1 |  | Sub-transmission line disconnection | A transmission outage occurred on the 110 kV line between Trbovlje and Beričevo I. The line was disconnected at the Trbovlje substation and remained out of service for several hours. The event was recorded in the operational report of the Slovenian transmission system operator ELES. | E |  | TECH | EQUIPMENT_FAILURE |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 3 | 2 | 3 | 0 | 4 | Official ELES report; 110 kV line outage with several-hour duration; regional transmission manifestation; no documented downstream disruption.
e_ops_2024_0513_001 | 2024_05_13 | E_OPS |  | DV 110 kV TE TOL–Beričevo outage unknown cause | 2024-05-13 | 14:09 | 2024-05-13 | 14:45 | 00:36 | <1h | Ljubljana 110 kV network zone | local | 1 |  | Short transmission interruption | A short outage occurred on the 110 kV line connecting TE TOL and Beričevo. The cause of the outage was not identified in the operational report. The disturbance lasted less than one hour and required inspection of the transmission line. | E |  | TECH | EQUIPMENT_FAILURE |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 3 | Short 110 kV line outage; cause not confirmed; local operational signal with limited duration and limited documented impact.
e_ops_2024_0515_001 | 2024_05_15 | E_OPS |  | Urgent shutdown PST 400/400 kV Divača Buchholz alarm | 2024-05-15 | 22:11 |  |  | 00:00 | <1h | RTP Divača substation | regional | 1 |  | Protection trip on phase shifting transformer | An urgent shutdown of the 400/400 kV phase shifting transformer at the Divača substation occurred following a Buchholz relay alarm. The equipment was disconnected as a protective measure and inspected by operators. | E |  | TECH | PROTECTION_TRIP |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 2 | 1 | 0 | 3 | Buchholz alarm and urgent PST shutdown; important transmission asset but incomplete duration/restoration detail lowers confidence.
e_ops_2024_0517_001 | 2024_05_17 | E_OPS |  | ČHE Avče temporary unavailability | 2024-05-17 | 08:00 | 2024-05-17 | 18:00 | 10:00 | 6–24h | ČHE Avče | regional | 1 |  | Generation limitation | Pumped storage plant Avče was unavailable due to repair works on air injection pipe. Pumped storage contributes to balancing and frequency support; unavailability reduces flexibility margins. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 2 | 3 | 0 | 4 | Pumped-storage relevance
e_ops_2024_0519_001 | 2024_05_19 | E_OPS |  | HE Zlatoličje generation limitation | 2024-05-19 | 12:00 | 2024-05-19 | 15:00 | 03:00 | 1–6h | HE Zlatoličje | local | 1 |  | Planned maintenance limitation | Power reduced to 100 MW during turbine intake cleaning. Planned maintenance with limited systemic significance. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 0 | 4 | Maintenance-related limitation
e_ops_2024_0521_001 | 2024_05_21 | E_OPS |  | Extended hydro limitation HE Vuzenica | 2024-05-21 | 14:00 | 2024-05-23 | 15:00 | 49:00 | 1–3d | HE Vuzenica hydropower plant | regional | 1 |  | Generation output limitation | A power output limitation was imposed on unit 3 at the Vuzenica hydropower plant due to a servomotor malfunction affecting turbine operation. The restriction lasted approximately two days before full capacity was restored. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 3 | 2 | 4 | 0 | 4 | Generation limitation at HE Vuzenica persisted about two days; moderate energy stress through prolonged reduced capacity.
e_ops_2024_0522_002 | 2024_05_22 | E_OPS |  | HE Zlatoličje generation limitation | 2024-05-22 | 11:00 | 2024-05-22 | 14:00 | 03:00 | 1–6h | HE Zlatoličje | local | 1 |  | Generation limitation | Hydropower plant Zlatoličje output was temporarily reduced during turbine intake cleaning operations. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly report | p.3 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 0 | 4 | Maintenance-related limitation
e_ops_2024_0522_001 | 2024_05_22 | E_OPS |  | 35 kV line outage Divača–Kozina storm related | 2024-05-22 | 13:13 | 2024-05-22 | 13:14 | 00:01 | <1h | Divača–Kozina transmission corridor | local | 1 |  | Storm related line outage | A short outage occurred on the 35 kV transmission line between Divača and Kozina during a convective storm event. The disturbance lasted approximately one minute before restoration of normal operation. | E |  | ENV | CONV_STORM |  |  | ELES_MAY_2024 | ELES monthly operational report (May 2024) | p.3 | pdf | official_report | A | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 4 | Storm-related short line outage; environmental forcing present but localized and brief; no documented broader effect.
e_ops_2024_0527_001 | 2024_05_27 | E_OPS |  | 220 kV line outage Kleče–Divača lightning | 2024-05-27 | 20:19 | 2024-05-27 | 20:27 | 00:08 | <1h | Kleče–Divača transmission corridor | regional | 1 |  | Lightning induced transmission line trip | A lightning strike during thunderstorm conditions triggered a short outage on the 220 kV transmission line between Kleče and Divača. The disturbance lasted several minutes before restoration. | E |  | ENV | CONV_STORM |  |  | ELES_MAY_2024 | ELES monthly operational report | p.3 | pdf | official_report | A | 2 | 1 | 0 | 0 | 2 | 2 | 1 | 0 | 4 | Lightning-induced 220 kV line outage; clear convective forcing; brief duration; regional transmission corridor involvement.
e_ops_2024_0527_002 | 2024_05_27 | E_OPS |  | 220 kV line outage Kleče–Divača lightning | 2024-05-27 | 22:11 | 2024-05-28 | 04:33 | 06:22 | 6–24h | Šoštanj thermal power plant | regional | 1 |  | Generation unit trip at thermal power plant | Generation unit 6 at the Šoštanj thermal power plant experienced an outage from 22:11 until 04:33 the following day. The cause of the outage was not specified in the operational report. | E |  | TECH | GENERATION_TRIP |  |  | ELES_MAY_2024 | ELES monthly operational report | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 3 | 2 | 3 | 0 | 4 | Large thermal generation unit trip with multi-hour outage; moderate energy-system stress; no documented cascade.
e_ops_2024_0527_003 | 2024_05_27 | E_OPS |  | TEŠ PT51/PT52 synchronization unavailable | 2024-05-27 | 22:30 | 2024-05-27 | 23:16 | 00:46 | <1h | TEŠ | local | 1 |  | Generation synchronization limitation | A major generation unit trip occurred at thermal power plant Šoštanj block 6. The unit remained offline until early morning. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly operational report | p.3 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 4 | Local synchronization limitation
e_ops_2024_0527_004 | 2024_05_27 | E_OPS |  | TEŠ PT51/PT52 synchronization unavailable | 2024-05-27 | 22:30 | 2024-05-27 | 23:16 | 00:46 | <1h | TEŠ | local | 1 |  | Generation synchronization limitation | Two synchronization units PT51 and PT52 were temporarily unavailable for synchronization during plant operation. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly report | p.3 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 4 | Local synchronization limitation
e_ops_2024_0528_001 | 2024_05_28 | E_OPS |  | PB1 EDT maintenance due to fault | 2024-05-28 | 00:25 | 2024-05-29 | 07:00 | 30:35 | 1–3d | EDT power plant | regional | 1 |  | Outage due to fuel-system fault | Maintenance due to malfunction in oil burner fuel supply system. Reduced thermal flexibility during the period. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly operational report | p.3 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 2 | 4 | 0 | 4 | Generation unit maintenance limitation
e_ops_2024_0530_001 | 2024_05_30 | E_OPS |  | HE Doblar 1 generation shutdown | 2024-05-30 | 10:00 | 2024-05-30 | 12:00 | 02:00 | 1–6h | HE Doblar 1 | local | 1 |  | Generation unit shutdown | A generating unit at hydropower plant Doblar 1 was shut down due to a fault in communication within the excitation control system. | E |  | TECH | GENERATION_TRIP |  |  | ELES_MAY_2024 | ELES monthly operational report | p.3 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 0 | 4 | Local hydropower shutdown
e_ops_2024_0531_001 | 2024_05_31 | E_OPS |  | HE Zlatoličje generation limitation | 2024-05-31 | 11:00 | 2024-05-31 | 15:00 | 04:00 | 1–6h | HE Zlatoličje | local | 1 |  | Intake cleaning limitation | Hydropower plant Zlatoličje output was temporarily reduced during turbine intake cleaning operations. | E |  | TECH | PLANNED_LIMITATION |  |  | ELES_MAY_2024 | ELES monthly operational report | p.3 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 0 | 4 | Maintenance related limitation
e_ops_2024_0601_001 | 2024_06_01 | E_OPS |  | ČHE Avče trip during pump startup | 2024-06-01 | 09:54 | 2024-06-01 | 10:35 | 00:41 | <1h | ČHE Avče | local | 1 |  | Pumped-storage startup trip | Trip during pump-mode startup; restored within about 40 minutes. | E |  | TECH | GENERATION_TRIP |  |  | ELES_2024_W22 | ELES weekly report W22 | events section | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 5 | Operational startup issue
e_ops_2024_0601_201 | 2024_06_01 | E_OPS |  | ČHE Avče trip during pump-mode start | 2024-06-01 | 09:54 | 2024-06-01 | 10:35 | 00:41 | <1h | ČHE Avče | regional | 1 |  | Pumped-storage trip during start in pumping mode | Trip of ČHE Avče at 09:54 during start-up procedure in pumping mode; availability restored from 10:35. Short-duration but relevant for flexibility and ancillary services availability. | E |  | TECH | GENERATION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 2 | 1 | 1 | 5 | Flexibility asset short outage
e_ops_2024_0605_001 | 2024_06_05 | E_OPS | CL_2024_0605_FORMIN_BUS | HE Formin units 1+2 trip busbar fault | 2024-06-05 | 08:50 | 2024-06-05 | 09:47 | 00:57 | <1h | HE Formin | local | 1 |  | Two hydro units trip | Simultaneous outage of units 1 and 2 due to busbar bay fault representing multi-asset hydro generation disturbance. | E |  | TECH | BUSBAR_FAULT |  |  | ELES_2024_W23 | ELES weekly report W23 | events | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5 | Confirmed shared cause
e_ops_2024_0605_301 | 2024_06_05 | E_OPS | CL_2024_0605_FORMIN_BUS | HE Formin unit 1 trip | 2024-06-05 | 08:50 | 2024-06-05 | 09:47 | 00:57 | <1h | HE Formin | local | 1 |  | Hydro unit trip due to busbar bay fault | HE Formin units 1 and 2 tripped from 08:50 to 09:47 due to a fault on the busbar bay, with 120 MW unavailable. This row records unit 1 as part of a two-unit simultaneous incident. | E |  | TECH | GENERATION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5 | Simultaneous two-unit trip
e_ops_2024_0605_302 | 2024_06_05 | E_OPS | CL_2024_0605_FORMIN_BUS | HE Formin unit 2 trip | 2024-06-05 | 08:50 | 2024-06-05 | 09:47 | 00:57 | <1h | HE Formin | local | 1 |  | Hydro unit trip due to busbar bay fault | Same incident as unit 1: busbar bay fault caused units 1 and 2 to trip simultaneously, resulting in 120 MW unavailable until 09:47. | E |  | TECH | GENERATION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5 | Simultaneous two-unit trip
e_ops_2024_0610_101 | 2024_06_10 | E_OPS |  | Safety shutdown TR T411 RTP Okroglo | 2024-06-10 | 12:00 | 2024-06-10 | 20:00 | 08:00 | 6–24h | RTP Okroglo | regional | 1 |  | Safety shutdown for corrective maintenance | Safety shutdown of TR T411 in RTP Okroglo from 12:00 to 20:00 to repair a fault on a support insulator of the 400 kV busbar system G2. The report frames this as a safety shutdown tied to corrective maintenance. | E |  | TECH | PLANNED_LIMITATION | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 3 | 1 | 5 | Planned/corrective shutdown explicitly stated
e_ops_2024_0611_001 | 2024_06_11 | E_OPS |  | DV 110 kV HE Dravograd–Žel. Ravne outage | 2024-06-11 | 07:19 | 2024-06-11 | 11:50 | 04:31 | 1–6h | HE Dravograd–Železarna Ravne | local | 1 |  | 110 kV line outage due to burned arc | Outage of the 110 kV line HE Dravograd–Žel. Ravne from 07:19 to 11:50. The report attributes the event to a burned arc on phase L3, indicating a clearly documented electrical fault on the line. | E |  | TECH | EQUIPMENT_FAILURE | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 1 | 2 | 1 | 5 | Cause explicitly stated
e_ops_2024_0612_001 | 2024_06_12 | E_OPS | CL_2024_0612_KIDRICEVO_BUS_S1 | RTP Kidričevo 110 kV busbar S I outage | 2024-06-12 | 05:10 | 2024-06-12 | 07:48 | 02:38 | 1–6h | RTP Kidričevo | regional | 1 |  | 110 kV busbar outage initiating multi-asset incident | Outage of 110 kV busbar S I in RTP Kidričevo from 05:10 to 07:48. Multiple connected transformers and 110 kV lines tripped in the same event window, but the monthly report gives no confirmed root cause. This row captures the common busbar element of the cluster. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 4 | 2 | 2 | 4 | 5 | Multi-asset substation incident
e_ops_2024_0612_002 | 2024_06_12 | E_OPS | CL_2024_0612_KIDRICEVO_BUS_S1 | TR T411 Beričevo emergency shutdown Buchholz alarm | 2024-06-12 | 05:10 | 2024-06-12 | 05:35 | 00:25 | <1h | RTP Kidričevo | local | 1 |  | Transformer outage during substation incident | Transformer TR I in RTP Kidričevo tripped during the 110 kV busbar S I incident and remained out of service until 05:35. Root cause is not identified in the report; treated as part of the Kidričevo multi-asset cluster. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 1 | 1 | 4 | 5 | Asset-level record within cluster
e_ops_2024_0612_003 | 2024_06_12 | E_OPS | CL_2024_0612_KIDRICEVO_BUS_S1 | RTP Kidričevo TR III outage | 2024-06-12 | 05:10 | 2024-06-12 | 05:38 | 00:28 | <1h | RTP Kidričevo | local | 1 |  | Transformer outage during substation incident | Transformer TR III in RTP Kidričevo tripped during the busbar incident and remained out until 05:38. Listed as part of the same Kidričevo cluster with unknown root cause. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 1 | 1 | 4 | 5 | Asset-level record within cluster
e_ops_2024_0612_004 | 2024_06_12 | E_OPS | CL_2024_0612_KIDRICEVO_BUS_S1 | RTP Kidričevo TR VII outage | 2024-06-12 | 05:10 | 2024-06-12 | 07:54 | 02:44 | 1–6h | RTP Kidričevo | regional | 1 |  | Transformer outage during substation incident | Transformer TR VII tripped in the same Kidričevo incident and remained unavailable until 07:54, representing the longest-lasting transformer outage inside the cluster. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 4 | 2 | 2 | 4 | 5 | Longest transformer impact in cluster
e_ops_2024_0612_005 | 2024_06_12 | E_OPS | CL_2024_0612_KIDRICEVO_BUS_S1 | DV 110 kV Breg–Kidričevo outage | 2024-06-12 | 05:10 | 2024-06-12 | 05:47 | 00:37 | <1h | Breg–Kidričevo | local | 1 |  | 110 kV line outage during substation incident | DV 110 kV Breg–Kidričevo tripped as part of the Kidričevo incident and remained out until 05:47. The report lists simultaneous outages of multiple transformers and lines connected to the same substation, with unknown root cause. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 1 | 1 | 4 | 5 | Asset-level record within cluster
e_ops_2024_0612_006 | 2024_06_12 | E_OPS | CL_2024_0612_KIDRICEVO_BUS_S1 | DV 110 kV Cirkovce–Kidričevo 1 outage | 2024-06-12 | 05:10 | 2024-06-12 | 07:48 | 02:38 | 1–6h | Cirkovce–Kidričevo | local | 1 |  | 110 kV line outage during substation incident | DV 110 kV Cirkovce–Kidričevo 1 tripped and remained out until 07:48 in the same time window as the Kidričevo busbar outage. Root cause reported as unknown. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 2 | 4 | 5 | Asset-level record within cluster
e_ops_2024_0612_007 | 2024_06_12 | E_OPS | CL_2024_0612_KIDRICEVO_BUS_S1 | DV 110 kV Cirkovce–Kidričevo 3 outage | 2024-06-12 | 05:10 | 2024-06-12 | 07:49 | 02:39 | 1–6h | Cirkovce–Kidričevo | local | 1 |  | 110 kV line outage during substation incident | DV 110 kV Cirkovce–Kidričevo 3 tripped and remained out until 07:49. Listed as part of the same Kidričevo substation incident with multiple simultaneous asset outages and unknown root cause. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 2 | 4 | 5 | Asset-level record within cluster
e_ops_2024_0612_101 | 2024_06_12 | E_OPS |  | Emergency shutdown T411 RTP Beričevo | 2024-06-12 | 12:30 |  |  |  |  | RTP Beričevo | regional | 1 |  | Emergency shutdown for Buchholz relay investigation | Emergency shutdown of T411 in RTP Beričevo starting at 12:30 for investigation of Buchholz relay operation. The monthly list does not provide a restoration timestamp. The event indicates potential incipient transformer/internal fault signal. | E |  | TECH | PROTECTION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 4 | 0 | 0 | 4 | 2 |  | 2 | 4 | End time not listed
e_ops_2024_0614_301 | 2024_06_14 | E_OPS |  | HE Vuzenica unit 2 trip | 2024-06-14 | 08:50 | 2024-06-14 | 09:18 | 00:28 | <1h | HE Vuzenica | local | 1 |  | Hydro unit trip due to governor fault | Trip of unit 2 at HE Vuzenica from 08:50 to 09:18 due to a main governor fault. | E |  | TECH | GENERATION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 5 | Cause explicitly stated
e_ops_2024_0614_302 | 2024_06_14 | E_OPS |  | HE Plave 2 unit 1 trip | 2024-06-14 | 19:47 | 2024-06-14 | 21:20 | 01:33 | 1–6h | HE Plave 2 | local | 1 |  | Hydro unit trip due to turbine governor control fault | Trip of unit 1 at HE Plave 2 from 19:47 to 21:20 due to a DTR fault on the turbine governor. | E |  | TECH | GENERATION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 1 | 0 | 0 | 2 | 1 | 2 | 1 | 5 | Cause explicitly stated
e_ops_2024_0616_201 | 2024_06_16 | E_OPS |  | ČHE Avče failed start / generator-mode unavailability | 2024-06-16 | 20:00 | 2024-06-16 | 23:00 | 03:00 | 1–6h | ČHE Avče | regional | 1 |  | Pumped-storage unavailable due to fuse fault | Failed start in generator mode / unavailability of ČHE Avče from 20:00 to 23:00 due to a fuse fault on the measuring transformer of the main switch. | E |  | TECH | EQUIPMENT_FAILURE | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 2 | 2 | 1 | 5 | Explicit fuse fault; flexibility impact
e_ops_2024_0617_001 | 2024_06_17 | E_OPS |  | HE Doblar 2 unit 1 trip | 2024-06-17 | 05:04 | 2024-06-17 | 05:26 | 00:22 | <1h | HE Doblar 2 | local | 1 |  | Hydro unit trip | Hydro generation unit trip with unspecified cause. | E |  | UNKNOWN | GENERATION_TRIP |  |  | ELES_2024_W25 | ELES weekly report W25 | events | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 4 | Isolated unit
e_ops_2024_0617_301 | 2024_06_17 | E_OPS |  | HE Doblar 2 unit 1 trip | 2024-06-17 | 05:04 | 2024-06-17 | 05:26 | 00:22 | <1h | HE Doblar 2 | local | 1 |  | Hydro unit trip unknown cause | Trip of unit 1 at HE Doblar 2 from 05:04 to 05:26. The report lists unknown cause. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 3 | Cause not provided
e_ops_2024_0618_301 | 2024_06_18 | E_OPS |  | HE Dravograd unit 2 outage | 2024-06-18 | 02:36 | 2024-06-18 | 08:10 | 05:34 | 1–6h | HE Dravograd | regional | 1 |  | Hydro unit outage due to guide vane positioning fault | Trip/outage of unit 2 at HE Dravograd from 02:36 to 08:10 due to a fault in the guide vane positioning subsystem. | E |  | TECH | GENERATION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 2 | 2 | 1 | 5 | Duration about 5.5h
e_ops_2024_0618_001 | 2024_06_18 | E_OPS |  | DV 220 kV Podlog–Žerjavinec outage | 2024-06-18 | 17:38 | 2024-06-18 | 20:50 | 03:12 | 1–6h | Podlog–Žerjavinec | cross-border | 1 |  | 220 kV interconnection outage | Outage of DV 220 kV Podlog–Žerjavinec from 17:38 to 20:50. The report states unknown cause. As this is a 220 kV cross-border corridor element, it is relevant for interconnection stress characterization. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 3 | 2 | 2 | 5 | Cross-border corridor; cause not provided
e_ops_2024_0619_302 | 2024_06_19 | E_OPS |  | HE Dravograd unit 2 trip | 2024-06-19 | 21:03 | 2024-06-19 | 21:29 | 00:26 | <1h | HE Dravograd | local | 1 |  | Hydro unit trip due to high pressure | Trip of unit 2 at HE Dravograd from 21:03 to 21:29 due to excessive pressure in the safety boiler. | E |  | TECH | GENERATION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 5 | Cause explicitly stated
e_ops_2024_0620_001 | 2024_06_20 | E_OPS |  | TR T412 400/110 kV RTP Cirkovce outage | 2024-06-20 | 17:40 | 2024-06-20 | 20:42 | 03:02 | 1–6h | RTP Cirkovce | regional | 1 |  | 400/110 kV transformer outage | Outage of TR T412 400/110 kV in RTP Cirkovce from 17:40 to 20:42. The report attributes the event to a pressure switch, indicating a technical/protection-related trigger. | E |  | TECH | PROTECTION_TRIP | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 2 | 1 | 5 | Cause explicitly stated
e_ops_2024_0620_201 | 2024_06_20 | E_OPS | CL_2024_0620_TES_SYNC | TEŠ PT51 synchronization difficulty | 2024-06-20 | 18:50 | 2024-06-21 | 00:32 | 05:42 | 1–6h | TEŠ | regional | 1 |  | Synchronization difficulty PT51 | The report states difficulties synchronizing TEŠ PT51 at 18:50 and PT52 at 19:20 on 20 June. Both units were again available at 00:32 on 21 June. This row captures PT51’s unavailability interval. | E |  | TECH | PLANNED_LIMITATION | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 2 | 2 | 5 | Grouped with PT52 under same sync incident
e_ops_2024_0620_202 | 2024_06_20 | E_OPS | CL_2024_0620_TES_SYNC | TEŠ PT52 synchronization difficulty | 2024-06-20 | 19:20 | 2024-06-21 | 00:32 | 05:12 | 1–6h | TEŠ | regional | 1 |  | Synchronization difficulty PT52 | Same TEŠ synchronization incident as PT51; PT52 synchronization difficulty began at 19:20 and both units were available again at 00:32 on 21 June. Recorded separately to preserve asset-level granularity. | E |  | TECH | PLANNED_LIMITATION | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 2 | 2 | 5 | Grouped with PT51 under same sync incident
e_ops_2024_0622_001 | 2024_06_22 | E_OPS |  | DV 110 kV Žiri–Idrija 2 trip | 2024-06-22 | 05:10 | 2024-06-22 | 05:13 | 00:03 | <1h | Žiri–Idrija | local | 1 |  | 110 kV line trip via distance protection | DV 110 kV Žiri–Idrija 2 tripped from 05:10 to 05:13 on distance protection. The report notes unknown cause. Short duration suggests rapid restoration. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 4 | Protection action; cause not specified
e_ops_2024_0626_001 | 2024_06_26 | E_OPS |  | DV 220 kV Podlog–Žerjavinec repeated outage | 2024-06-26 | 15:39 | 2024-06-26 | 19:46 | 04:07 | 1–6h | Podlog–Žerjavinec | cross-border | 1 |  | Repeated 220 kV interconnection outage | Second listed outage of DV 220 kV Podlog–Žerjavinec in June, from 15:39 to 19:46, with unknown cause. Repetition within one month suggests corridor vulnerability, but the report does not provide attribution. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 3 | 2 | 2 | 5 | Repeat outage on same corridor
e_ops_2024_0627_001 | 2024_06_27 | E_OPS |  | DV 110 kV Murska Sobota–Mačkovci storm trip | 2024-06-27 | 02:33 | 2024-06-27 | 02:37 | 00:04 | <1h | Murska Sobota–Mačkovci | local | 1 |  | 110 kV storm-related trip | DV 110 kV Murska Sobota–Mačkovci tripped from 02:33 to 02:37; the report explicitly states storm as the cause. | E |  | ENV | CONV_STORM | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 5 | Weather driver explicit
e_ops_2024_0629_001 | 2024_06_29 | E_OPS |  | DV 220 kV Kleče–Divača outage | 2024-06-29 | 10:06 | 2024-06-29 | 15:39 | 05:33 | 1–6h | Kleče–Divača | regional | 1 |  | 220 kV corridor outage | Outage of DV 220 kV Kleče–Divača from 10:06 to 15:39 with unknown cause. As a major internal corridor, this represents notable operational stress. | E |  | UNKNOWN | UNDETERMINED | file:Junij_2024.pdf |  | ELES_2024_06 | ELES monthly operational report (June 2024) | p.3/6 | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 2 | 1 | 4 | Major corridor; cause not specified
e_ops_2024_0708_001 | 2024_07_08 | E_OPS |  | DV 110 kV Formin–Nedeljanec one-sided outage | 2024-07-08 | 15:55 | 2024-07-08 | 16:50 | 00:55 | <1h | RTP Nedeljanec | local | 1 |  | One-sided 110 kV line outage | One-sided 110 kV line outage. Event recorded as 'DV 110 kV Formin–Nedeljanec one-sided outage'. Location: RTP Nedeljanec. Coded as UNKNOWN / UNDETERMINED. | E |  | UNKNOWN | UNDETERMINED |  |  | ELES_2024_W28 | ELES weekly report W28 | events | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 1 | 1 | 1 | 5
e_ops_2024_0711_001 | 2024_07_11 | E_OPS |  | ČHE Avče pump-mode trip undervoltage | 2024-07-11 | 13:59 | 2024-07-11 | 15:20 | 01:21 | 1–6h | ČHE Avče | local | 1 |  | Pumped-storage trip | Trip in pump mode due to undervoltage protection. | E |  | TECH | UNDER_VOLTAGE_PROTECTION |  |  | ELES_2024_W28 | ELES weekly report W28 | events | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 5
e_ops_2024_0712_001 | 2024_07_12 | E_OPS |  | DV 110 kV TE TOL–Črnuče trip (storm) | 2024-07-12 | 15:22 | 2024-07-12 | 15:25 | 00:03 | <1h | TE TOL–Črnuče | local | 1 |  | 110 kV trip due to storm | 110 kV trip due to storm. Event recorded as 'DV 110 kV TE TOL–Črnuče trip (storm)'. Location: TE TOL–Črnuče. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W28 | ELES weekly report W28 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 5
e_ops_2024_0717_001 | 2024_07_17 | E_OPS | CL_2024_0717_OKROGLO_JEKLARNA_LIGHTNING | DV 110 kV Okroglo–Jeklarna I+II lightning trips | 2024-07-17 | 23:16 | 2024-07-17 | 23:23 | 00:07 | <1h | Okroglo–Jeklarna | local | 1 |  | Double circuit lightning trip | Lightning trip circuit I. Event recorded as 'DV 110 kV Okroglo–Jeklarna I lightning trip'. Location: Okroglo–Jeklarna. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W29 | ELES weekly report W29 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5 | Parallel circuit event
e_ops_2024_0717_002 | 2024_07_17 | E_OPS | CL_2024_0717_OKROGLO_JEKLARNA_LIGHTNING | DV 110 kV Okroglo–Jeklarna II lightning trip | 2024-07-17 | 23:16 | 2024-07-17 | 23:23 | 00:07 | <1h | Okroglo–Jeklarna | local | 1 |  | Lightning trip circuit II | Lightning trip circuit II. Event recorded as 'DV 110 kV Okroglo–Jeklarna II lightning trip'. Location: Okroglo–Jeklarna. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W29 | ELES weekly report W29 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5
e_ops_2024_0718_001 | 2024_07_18 | E_OPS | CL_2024_0718_400KV_FIRE | DV 400 kV Divača–Redipuglia safety shutdown fire | 2024-07-18 | 13:03 | 2024-07-19 | 00:05 | 10:02 | 6–24h | Cross-border corridor | regional | 1 |  | 400 kV corridor fire shutdown | Emergency safety shutdown due to wildfire extinguishing near line. | E |  | ENV | WILDFIRE_PROXIMITY |  |  | ELES_2024_W29 | ELES weekly report W29 | events | pdf | official_report | A | 3 | 4 | 0 | 0 | 4 | 4 | 3 | 2 | 5 | Cross-border impact
e_ops_2024_0719_001 | 2024_07_19 | E_OPS | CL_2024_0719_VUZENICA_VUHRED_STORM | DV 400 kV Divača–Redipuglia safety shutdown repeat | 2024-07-19 | 20:49 | 2024-07-19 | 21:26 | 00:37 | <1h | Vuzenica–Vuhred | local | 1 |  | Repeated wildfire safety shutdown | Distance protection storm trip. Event recorded as 'DV 110 kV HE Vuzenica–Vuhred south trip'. Location: Vuzenica–Vuhred. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W29 | ELES weekly report W29 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5 | Same corridor cluster
e_ops_2024_0719_002 | 2024_07_19 | E_OPS | CL_2024_0719_VUZENICA_VUHRED_STORM | DV 110 kV HE Vuzenica–Vuhred north trip | 2024-07-19 | 20:49 | 2024-07-19 | 21:26 | 00:37 | <1h | Vuzenica–Vuhred | local | 1 |  | Distance protection storm trip | Distance protection storm trip. Event recorded as 'DV 110 kV HE Vuzenica–Vuhred north trip'. Location: Vuzenica–Vuhred. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W29 | ELES weekly report W29 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5
e_ops_2024_0720_001 | 2024_07_20 | E_OPS |  | DV 110 kV Ljutomer–Murska Sobota trip | 2024-07-20 | 02:59 | 2024-07-20 | 03:04 | 00:05 | <1h | Ljutomer–Murska Sobota | local | 1 |  | Storm induced trip | Storm induced trip. Event recorded as 'DV 110 kV Ljutomer–Murska Sobota trip'. Location: Ljutomer–Murska Sobota. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W29 | ELES weekly report W29 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 5
e_ops_2024_0722_001 | 2024_07_22 | E_OPS |  | HE Vuhred unit 2 trip overheating cable ignition | 2024-07-22 | 06:57 | 2024-07-22 | 12:43 | 05:46 | 1–6h | HE Vuhred | local | 1 |  | Hydro excitation transformer fault | Overheating joint and cable ignition on secondary side of excitation transformer. | E |  | TECH | OVERHEATING_FIRE |  |  | ELES_2024_W30 | ELES weekly report W30 | events | pdf | official_report | A | 1 | 2 | 0 | 0 | 3 | 1 | 2 | 1 | 5
e_ops_2024_0729_001 | 2024_07_29 | E_OPS | CL_2024_0729_SWITCHING_PODLOG | DV 110 kV Trbovlje–Brestanica emergency shutdown | 2024-07-29 | 07:12 | 2024-07-29 | 07:35 | 00:23 | <1h | Šoštanj–Podlog | regional | 1 |  | Switching manipulation error | Switching manipulation error. Event recorded as 'DV 400 kV Šoštanj–Podlog outage switching error'. Location: Šoštanj–Podlog. Coded as TECH / HUMAN_ERROR_SWITCHING. | E |  | TECH | HUMAN_ERROR_SWITCHING |  |  | ELES_2024_W31 | ELES weekly report W31 | events | pdf | official_report | A | 0 | 4 | 0 | 0 | 4 | 3 | 1 | 4 | 5
e_ops_2024_0729_003 | 2024_07_29 | E_OPS | CL_2024_0729_SWITCHING_PODLOG | TEŠ Block 6 outage due to corridor outage | 2024-07-29 | 07:13 | 2024-07-29 | 17:24 | 10:11 | 6–24h | TEŠ | regional | 1 |  | Cascade from 400 kV outage | Cascade from 400 kV outage. Event recorded as 'TEŠ Block 6 outage due to corridor outage'. Location: TEŠ. Coded as TECH / GENERATION_OUTAGE. | E |  | TECH | GENERATION_OUTAGE |  |  | ELES_2024_W31 | ELES weekly report W31 | events | pdf | official_report | A | 0 | 4 | 0 | 0 | 4 | 3 | 3 | 4 | 5
e_ops_2024_0729_002 | 2024_07_29 | E_OPS |  | DV 110 kV Trbovlje–Brestanica emergency outage | 2024-07-29 | 12:43 | 2024-07-29 | 13:30 | 00:47 | <1h | Trbovlje | local | 1 |  | Breaker gas pressure low | Breaker gas pressure low. Event recorded as 'DV 110 kV Trbovlje–Brestanica emergency outage'. Location: Trbovlje. Coded as TECH / BREAKER_GAS_PRESSURE_LOW. | E |  | TECH | BREAKER_GAS_PRESSURE_LOW |  |  | ELES_2024_W31 | ELES weekly report W31 | events | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 1 | 1 | 2 | 5
e_ops_2024_0801_001 | 2024_08_01 | E_OPS | CL_2024_0801_DIVACA_LIGHTNING | DV 110 kV Divača–Dekani lightning trip | 2024-08-01 | 21:56 | 2024-08-01 | 21:59 | 00:03 | <1h | Divača–Dekani | local | 1 |  | Lightning corridor event | Lightning corridor event. Event recorded as 'DV 110 kV Divača–Dekani lightning trip'. Location: Divača–Dekani. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W31 | ELES weekly report W31 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5
e_ops_2024_0801_002 | 2024_08_01 | E_OPS | CL_2024_0801_DIVACA_LIGHTNING | DV 110 kV Divača–Izola lightning trip | 2024-08-01 | 21:56 | 2024-08-01 | 22:13 | 00:17 | <1h | Divača–Izola | local | 1 |  | Lightning corridor event | Lightning corridor event. Event recorded as 'DV 110 kV Divača–Izola lightning trip'. Location: Divača–Izola. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W31 | ELES weekly report W31 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 2 | 5
e_ops_2024_0802_001 | 2024_08_02 | E_OPS |  | DV 400 kV Heviz–Cirkovce outage | 2024-08-02 | 18:57 | 2024-08-02 | 21:50 | 02:53 | 1–6h | Heviz–Cirkovce | cross-border | 1 |  | Cross-border corridor outage | Cross-border corridor outage. Event recorded as 'DV 400 kV Heviz–Cirkovce outage'. Location: Heviz–Cirkovce. Coded as UNKNOWN / INTERCONNECTION_OUTAGE. | E |  | UNKNOWN | INTERCONNECTION_OUTAGE |  |  | ELES_2024_W31 | ELES weekly report W31 | events | pdf | official_report | A | 0 | 4 | 0 | 0 | 4 | 4 | 2 | 2 | 4
e_ops_2024_0807_001 | 2024_08_07 | E_OPS |  | DV 220 kV Beričevo–Podlog outage | 2024-08-07 | 17:40 | 2024-08-07 | 20:42 | 03:02 | 1–6h | Beričevo–Podlog | regional | 1 |  | 220 kV corridor outage | 220 kV corridor outage. Event recorded as 'DV 220 kV Beričevo–Podlog outage'. Location: Beričevo–Podlog. Coded as UNKNOWN / LINE_OUTAGE. | E |  | UNKNOWN | LINE_OUTAGE |  |  | ELES_2024_W32 | ELES weekly report W32 | events | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 2 | 2 | 1 | 4
e_ops_2024_0807_002 | 2024_08_07 | E_OPS |  | DV 110 kV Črnuče–Kleče storm trip | 2024-08-07 | 20:31 | 2024-08-07 | 20:39 | 00:08 | <1h | Črnuče–Kleče | local | 1 |  | Storm line trip | Storm line trip. Event recorded as 'DV 110 kV Črnuče–Kleče storm trip'. Location: Črnuče–Kleče. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W32 | ELES weekly report W32 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 5
e_ops_2024_0807_003 | 2024_08_07 | E_OPS |  | DV 110 kV HE Vuzenica–Vuhred one-sided outage | 2024-08-07 | 22:09 | 2024-08-07 | 22:49 | 00:40 | <1h | Vuhred | local | 1 |  | One-sided line outage | One-sided line outage. Event recorded as 'DV 110 kV HE Vuzenica–Vuhred one-sided outage'. Location: Vuhred. Coded as UNKNOWN / UNDETERMINED. | E |  | UNKNOWN | UNDETERMINED |  |  | ELES_2024_W32 | ELES weekly report W32 | events | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 3
e_ops_2024_0808_101 | 2024_08_08 | E_OPS |  | DV 110 kV Črnuče–Kleče emergency outage remediation | 2024-08-08 | 08:04 | 2024-08-08 | 12:43 | 04:39 | 1–6h | Kleče | local | 1 |  | Corrective maintenance outage | Corrective maintenance outage. Event recorded as 'DV 110 kV Črnuče–Kleče emergency outage remediation'. Location: Kleče. Coded as TECH / MAINTENANCE_CORRECTIVE. | E |  | TECH | MAINTENANCE_CORRECTIVE |  |  | ELES_2024_W32 | ELES weekly report W32 | events | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 1 | 2 | 1 | 5
e_ops_2024_0808_001 | 2024_08_08 | E_OPS |  | DV 400 kV Cirkovce–Podlog outage | 2024-08-08 | 14:37 | 2024-08-08 | 18:41 | 04:04 | 1–6h | Cirkovce–Podlog | regional | 1 |  | 400 kV outage unknown cause | 400 kV corridor outage. Event recorded as 'DV 400 kV Cirkovce–Podlog outage'. Location: Cirkovce–Podlog. Coded as UNKNOWN / LINE_OUTAGE. | E |  | UNKNOWN | LINE_OUTAGE |  |  | ELES_2024_W32 | ELES weekly report W32 | events | pdf | official_report | A | 0 | 4 | 0 | 0 | 4 | 3 | 2 | 2 | 4
e_ops_2024_0808_002 | 2024_08_08 | E_OPS |  | DV 110 kV Šoštanj–Mozirje outage | 2024-08-08 | 21:51 | 2024-08-08 | 21:53 | 00:02 | <1h | Šoštanj | local | 1 |  | Short 110 kV outage | Short line outage. Event recorded as 'DV 110 kV Šoštanj–Mozirje outage'. Location: Šoštanj. Coded as UNKNOWN / UNDETERMINED. | E |  | UNKNOWN | UNDETERMINED |  |  | ELES_2024_W32 | ELES weekly report W32 | events | pdf | official_report | A | 0 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 3
e_ops_2024_0812_001 | 2024_08_12 | E_OPS |  | DV 220 kV Podlog–Žerjavinec distance protection trip | 2024-08-12 | 18:23 | 2024-08-12 | 21:12 | 02:49 | 1–6h | Podlog–Žerjavinec | cross-border | 1 |  | Distance protection corridor trip | Distance protection corridor trip. Event recorded as 'DV 220 kV Podlog–Žerjavinec distance protection trip'. Location: Podlog–Žerjavinec. Coded as UNKNOWN / INTERCONNECTION_DISTANCE_PROTECTION. | E |  | UNKNOWN | INTERCONNECTION_DISTANCE_PROTECTION |  |  | ELES_2024_W33 | ELES weekly report W33 | events | pdf | official_report | A | 0 | 3 | 0 | 0 | 3 | 3 | 2 | 2 | 4
e_ops_2024_0814_001 | 2024_08_14 | E_OPS |  | DV 110 kV Brestanica–Krško NEK outage storm | 2024-08-14 | 08:31 | 2024-08-14 | 10:38 | 02:07 | 1–6h | Brestanica–Krško | regional | 1 |  | Likely storm outage near NEK corridor | Likely storm outage near NEK corridor. Event recorded as 'DV 110 kV Brestanica–Krško NEK outage storm'. Location: Brestanica–Krško. Coded as ENV / CONV_STORM. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W33 | ELES weekly report W33 | events | pdf | official_report | A | 2 | 3 | 0 | 0 | 3 | 2 | 2 | 1 | 4
e_ops_2024_0818_001 | 2024_08_18 | E_OPS |  | DV 110 kV Murska Sobota–Mačkovci storm trip | 2024-08-18 | 17:58 | 2024-08-18 | 18:35 | 00:37 | <1h | Murska Sobota | local | 1 |  | Storm HV trip | Lightning/thunderstorm trip. | E |  | ENV | CONV_STORM |  |  | ELES_2024_W33 | ELES weekly report W33 | events | pdf | official_report | A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 1 | 5